## Summary -Project Cost & Phasing
Particulars | Project Cost 220/11 kV | Developed, Owned, Operated by | Scope | Paid for by | Basis | CAPEX PHASING
| (Rs. Crores) |  |  |  | Basis | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | Total
2 Nos. independent 220 kV feeders including bays and transmission lines from 220 kV Jalpura and KP-5 GIS Substations of UPPTCL including GST | 52.89 | UPPTCL | Transmission | NIDP | UPPTCL Estimate (Paid in Actuals)
Contingency@10% | 5.289 |  |  |  | Contigency for UPPTCL Cost variation (if any)
Total Cost - Transmission Network (A) | 58.179 |  |  |  |  | 52.89 | 5.289 | 0 | 0 | 0 | 0 | 0 | 0 | 58.179
Metering Equipment - 220 kV - T/D Interface including GST | 1.5 | NIDP | Distribution | NIDP | NPCL Estimate | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5
220/11 kV Substation including 7 Nos. 220/11 kV transformers of 55 MVA each including GST | 75.0342 |  |  |  | POs/budgets Attached | 26.262 | 26.262 | 0 | 22.5102 | 0 | 0 | 0 | 0 | 75.0342
Downstream 11 kV Distribution Network including consumer metering including GST | 4.071 |  |  |  | Estimate Attached | 0 | 1.2213 | 0 | 2.8497 | 0 | 0 | 0 | 0 | 4.071
Land | 2.47 |  |  |  |  | 2.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47
G&A Expenses | 0.5 |  |  |  | Budgeted Estimate | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
Consultancy Expenses | 0.54 |  |  |  | Budgeted Estimate | 0.27 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54
Other Expenses, if any | 1 |  |  |  | Budgeted Estimate | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Contingency@10% | 8.5115 |  |  |  | Industry practice | 0 | 4.2558 | 0 | 4.2558 | 0 | 0 | 0 | 0 | 8.5115
Total Cost - Distribution Network (B) | 93.6267 |  |  |  |  | 29.752 | 34.259 | 0 | 29.6157 | 0 | 0 | 0 | 0 | 93.6267
Total (A+B) | 151.8057 |  |  |  |  | 82.642 | 39.548 | 0 | 29.6157 | 0 | 0 | 0 | 0 | 151.8057
% Phasing of Capex |  |  |  |  | UOM | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | Total
Transmission Cost - UPPTCL |  |  |  |  | % | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 200
Metering Equipment - 220 kV - T/D Interface |  |  |  |  | % | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100
220/11 kV Substation including 7 Nos. 220/11 kV transformers of 55 MVA Each |  |  |  |  | % | 35 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 100
Downstream 11 kV Distribution Network |  |  |  |  | % | 0 | 30 | 0 | 70 | 0 | 0 | 0 | 0 | 100
Land |  |  |  |  | % | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100
G&A Expenses |  |  |  |  | % | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 100
Consultancy Expenses |  |  |  |  | % | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 100
Other Expenses, if any |  |  |  |  | % | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 100
Contingency@10% |  |  |  |  | % | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 100
Summary of Capital Cost of 220/11kV distribution infrastructure , Phasing and Load
| Sr. No. | Particulars | Phase – I | Phase – I | Phase – II (FY 26)
|  |  | (FY 23) | (FY 24)
| 1 | Major Equipment’s | · 220 kV Incoming Metering and Transformer Bay Switchgear
|  |  | · 3x55MVA 220/11kV Transformers |  | 4x55MVA 220/11kV Transformers
|  |  | · 3 x 11 kV Switchgear + Metering Panels |  | 4 x 11 kV Switchgear + Metering Panels
| 2 | Capex | ₹ 29.8 Cr | ₹ 34.3 Cr | ₹29.6 Cr
| 3 | Loads | DC-1 and DC-2 (~90 MVA) |  | DC-3 TO DC-7 ( 110 ~160 MVA)

## 220kV Capex
220 KV NIDP Substation Cost
Item Description | UOM | Qty | Rate Rs | Total Amount Rs. | Remarks
Civil Construction Base Cost | LS |  |  | 26802662.1938 | As per WO
220KV AIS Switchyard Cost | LS |  |  | 245000000 | As per WO
Transformer 220/11kV - 50/55 mVA | Nos | 7 | 50000000 | 350000000 | Estimated as per PO
HT Metering for feeders | Nos | 8 | 100000 | 800000 | Budgeted Estimate
Real Time Monitoring | LS |  |  | 2500000 | Budgeted Estimate
Misc | Job | 1 | 10000000 | 10000000 | Missc Works
11 KV Scope
11kV cables+installation | Meter | 9000 | 2700 | 24300000 | Budgeted Estimate
GI Cable tray with support-600mm | Meter | 700 | 2200 | 1540000 | Budgeted Estimate
Termination 11kV cable | Nos | 72 | 20000 | 1440000 | Budgeted Estimate
11kV switchgear+ Metering Panel | Nos | 8 | 1000000 | 8000000 | Budgeted Estimate
TOtal |  |  |  | 670382662.1938
Total (Rs. Crores) |  |  |  | 67.0383 | Cr
67.0383
Tax |  |  |  | 12.0669 | GST @18%
Total (Including GST) |  |  |  | 79.1052 | Cr

## Civil Structural BOQ
C/9525/2022 |  |  | 10th August 2022
PROPOSED SUBSTATION 2 BUILDING FOR NOIDA DC PARK , NOIDA
Structure - Ground + 1st floor + Terrace
Approximate Estimated Quantites
Sr. No | Description of Item | Unit | Quantity | Rate | Amount
1 | Earth work (Excavation & Back filling)
Carrying out excavation in all types of soil viz dense, loose and soft murrum, carrying out demolition of any existing concrete portion, if encountered using suitable mechanical excavator and manually wherever required up to required level for casting of foundation as shown in the drawing to the satisfaction of EIC. Obtaining necessary statutory approvals / permissions viz drainage approval, royalty permission, debris management plan for excavation shall form part of excavation contractor's scope of work. The scope of work shall also include carting away and disposing of the debris muck at an approved location as approved by the regulatory authority and in consultation with the Engineer In Charge (EIC). The contractor shall take into account installation, maintainance and operation of approved dewatering system as required to ensure clear working area. During excavation all related records, levels shall be maintained by the contractor.
Adequate precaution need to be taken by covering the loaded vehicle with plastic or tarpauline before getting out of site so as to avoid fall and spread of any excavated material on road. Vehicle tyres shall be cleaned before vehicle movement out of site. The contractor to make proper arrangements and shall provide necessary shoring & shrutting to avoid any soil collapse. For measurement purpose, plan area x depth. All safety norms & regulation shall be strictly followed. General house keeping and surrounding area shall be kept neat and clean on a regular basis.
1.1 | Carrying out excavation in all types of soils including dense soil, filled up earth, clayee soil, sandy soil etc and carrying out demolition of any existing concrete portion, if encountered, using suitable mechanical excavator with a bucket attachment or manually wherever required up to required level for casting of foundation as shown in the drawing to the satisfaction of Project Manager.
i | From -0.00 m to -1.50 m level. | Cu.m | 662 | 170 | 112540
ii | From -1.50 m to -3.00 m level. | Cu.m | 530 | 190 | 100700
iii | From -3.00 m to -4.50 m level. | Cu.m | R.O | 300
1.2 | Excavation Item same as 1.1 but in all types of weathered / soft / disintegrated rock / localized boulders etc using a bucket and scraper attachment and no breaker or compressor jack hammer is required to be used for breaking this substrata, for excavating up to required level & depth as shown in the drawing.
i | From -0.00 m to -1.50 m level. | Cu.m | R.O | 1200
ii | From -1.50 m to -3.00 m level. | Cu.m | R.O | 1400
1.3 | Excavation item same as 1.1 but in all types of hard rock / basaltic / granitic rocks using the breaker attachment only to excavate through up to required level & depth as shown in the drawing.
i | From -0.00 m to -1.50 m level. | Cu.m | R.O | 1800
ii | From -1.50 m to -3.00 m level. | Cu.m | R.O | 2150
1.4 | Backfilling.
i | Back Filling:- Back filling in and around the foundation and at basement level with soil available within the plot laid in layers of not exceeding 300 mm thick including breaking clods, watering, compacting each layers with vibratory compactor to achieve 90 to 95% proctor density at optimum moisture content. At an inaccessible place the compaction shall be using with wooden / steel rammers. The scope of work shall include necessary leads and lifts, cost of conveyance of all materials within the site premises, required labour, machinery etc complete. Important Note - It is considered that sufficient space is available in the plot and soil quantity for backfilling shall be used from soil available at site. ( considered 25 % of total backfilling) | Cu.m | 350 | 90 | 31500
ii | Back Filling:- Backfilling with approved quality soil / Murum in and around footing and at basement level brought from outside ,laid in layers of not exceeding 300 mm thick including breaking clods, watering, compacting each layers with vibratory compactor to achieve 90 to 95% proctor density at optimum moisture content. At an unaccesible place the compaction shall be done using wooden / steel rammers. The scope of work shall include necessary leads and lifts, cost of conveyance of all materials within the site premises, required labour, machinery etc complete. (considered 75 % of total backfilling) | Cu.m | 1048 | 420 | 440160
iii | Carriage of material for excavated soil, clayey soil, sandy soil over a distance as directed by Engineer in charge etc complete. | Cu.m | 843 | 150 | 126450
Total of Excavation & Back filling
2 | Miscellaneous works
2.1 | Granular sub base :-Providing and laying 230mm thick granular sub base below grade slab at ground level as shown in the structural drawing using approved quality stone of appropriate thickness provided as shown in the drawing including the cost of base preparation by mechanical compaction, using hand broken metal/ Rubble and smaller pebbles for void filling, murum for binding as directed by the Engineer-in-charge including watering, packing, compaction etc.complete. The item includes all lead & lift. | Sq.m | 620 | 680 | 421600
2.2 | Antitermite treatment :- Providing Antitermite treatment in accordance with stipulations laid down by IS 6313-part II by approved agency with minimum of 10 years of guarantee including the cost of chemical, precautionary measures etc. complete at plinth level. | Sq.m | 835 | 90 | 75150
2.3 | Screed :- Providing & laying of 50mm thick CM 1:4 protective screed admixed with Integral waterproofing compound of approved make as per manufacturers specification at ground floor & 1st floor as shown in structural / arch drawings and as per Engineer in charge etc complte. | Sqm | 1326 | 550 | 729300
Total of Miscellaneous works
3 | Plain Cement Concrete (PCC) and Reinforced Cement Concrete (RCC) Works.
General Notes - The unit rate shall take into account the following …..
a | The Concrete used shall be 'Controlled Concrete'. Providing / Supplying, pumping and laying controlled concrete conforming to grades as specified in IS 456 and as per the specifications using mix approved by the consultant. Concrete shall be dense & crack free.
b | Contractor is advised to study the drawings before submission of the quote.
c | The mix design shall be carried out in accordance to the relevant IS Codes, in approved lab and the same shall be approved by the Structural Consultant. For mix design of all concrete grades, fly ash content shall not exceed a maximum of 25 % and in case of GGBS it would be 40%.
d | Designing of the mix, batching, mechanical mixing, transport, pumping and placing at all heights and location, all shapes and sizes, laying to required slopes, vibrating, curing and finishing, scaffolding, hacking the concrete surface, plant and machinery, hire and fuel, incidental charges, deshuttering, cutting of formwork for passing services, conduits, or for dowels etc complete to finish the work etc complete
e | Contractor shall maintain a certified testing lab at site with a minimum facilities / equipments as decided by the Project Manager for conducting Cube tests, sieve analysis and slump cone test.
f | Contractor shall rectify all water leakages in concrete with proper grouting and shall deem to be included in the unit rates.
g | All testing and quality assurance shall be as per tender specifications / conditions and shall deemed to be included in rates.
h | The scope shall also include protecting, curing of concrete surfaces as directed, dewatering (if applicable), concreting by either pumping or by approved mechanized means only.
i | Ready Mix Concrete shall be procured from approved manufacturer.
j | The rate for RCC work shall include forming of projections, sinking of floors in toilets or wherever required, keeping provision in shuttering for niches, dowel bars etc.
k | The contractors shall co-ordinate with other agencies appointed for services viz laying conduits, placing boxes, pipes, clamps etc.
l | The scope also includes necessary surface preparation providing and applying Aqua bond 150 or equivalent as a bonding agent and cement 1:1 proportion for construction joints as per manufacturer specifications.
m | Concrete rates are exclusive of formwork. Unless otherwise specified, formwork shall be measured and paid under item no 4 & Reinforcement under item No. 5.
n | After concreting the concrete shall be cured & covered with Hessian cloth for minimum 7 days.
o | The contractor shall take all necessary precautions for concreting operations during Summer season / hot weather to avoid direct exposure of laid concrete OR during Monsoon (rainy) season to avoid mixing of water with laid concrete.
p | In no case any defective concrete in any of the structural elements shall be acceptable. The contractor shall undertake remedial measures as instructed by the Structural Consultant. The remedial measures shall be smoothly finished with CM 1:4 at no extra cost. Any undulations, bulging etc shall be chipped and finished by the contractor without any extra cost.
q | Providing and laying swellable Water Stopper " Formdex 2010" of Hitchins or equivalent in position at all vertical & horizontal construction joints detailing
3.1 | Plain Cement Concrete (PCC) Works.
Providing and Laying M 10 grade PCC, specified thickness as shown in the drawing including compaction, curing, vibration etc complete. On clearance of the area by the excavation contractor, including clearing of muck & cleaning of the affected portion. The contractor shall take this activity into account while quoting for PCC. Minimum cementitious content shall be 300 Kg/m³.
i | 150mm thick below footings | Cu.m | 45 | 5950 | 267750
ii | 75mm thick below plinth beams and at plinth level | Cu.m | 169 | 5950 | 1005550
3.2 | Reinforced Cement Concrete
Providing & laying plant mixed design mix reinforced cement concrete conforming to grades as specified in (IS 456 - 2000) and as per specifications mentioned below at all levels using 20mm & down size aggregates, fine aggregates,OPC, necessary admixtures approved by Consultants, including designing the mix, trial cubes,acelerated curing, weigh batching, mechanical mixing, transporting, pumping and placing at all levels, excluding the cost of steel reinforcement, centering, shuttering but inclusive of cost towards pumping using line pump or boom placer, scaffolding, compacting with vibrators, construction joint treatments /expansion strips, curing and hacking the exposed surfaces wherever required to receive plaster or floated steel troweled surface whenever specified. The rate shall include cost of arrangements to provide recesses to slabs, columns, walls and placing and securing properly within the formwork sleeves and / or opening in slabs, construction joints, laying to required shape, size and slope all as per drawings.
Cost to include appropriate dewatering wherever necessary, cost of all materials, labours, all lead and lifts, tools, plant and machinery, hire and fuel charges and all other incidental charges etc., all as per specifications, drawings and as directed.Manufactured sand from approved makes can be considered. The scope also includes for providing cover to reinforcement.
3.2.1 | Ready mix concrete of M30 grade for various concrete elements with minimum cementitious content shall be 410 Kg per Cu.m.
i | Footings | Cum | 142 | 7600 | 1079200
ii | Columns at all levels | Cum | 66 | 7900 | 521400
iii | Slabs at all levels | Cum | 170 | 7800 | 1326000
iv | Beams at all levels | Cum | 210 | 7800 | 1638000
v | staircase slabs at all levels | Cum | 2 | 9000 | 18000
vi | cantilever slabs at all levels | Cum | 1 | 9000 | 9000
vii | Parapet wall at terrace level | Cum | 26 | 9000 | 234000
viii | Cornices at terarce level | Rmt | 170 | 2100 | 357000
3.2.2 | Ready mix concrete of M25 grade for various concrete elements with minimum cementitious content shall be 390 Kg per Cu.m. (notional quantity) | Cu.m | 3 | 8250 | 24750
3.2.3 | Ready mix concrete of M20 grade for various concrete elements with minimum cementitious content shall be 385 Kg per Cu.m.
i | Grade slab at ground level | Cu.m | 93 | 7500 | 697500
Total for PCC & Reinforced Cement Concrete work
4 | Shuttering works
4.1 | Providing, erecting, fixing in position plastic coated waterproof plywood shuttering of minimum thickness not less than 12 mm at all locations for all shapes with chamfers, splays, keys, wedges, props, bracings, nails, brackets, Acrow spans etc complete including close hacking of exposed concrete surface, deshuttering of the same after specified period without damaging the concrete works as directed by Engineer-in-charge, cutting holes for pipes etc. Providing and applying approved form oil on all surfaces of formwork coming in contact with concrete as per specifications and drawings and as directed by EIC. Area of formwork in contact with concrete shall be measured for payment. Area of any stop boards for construction joints shall not be measured. Stagging height shall be as shown in the drawing. The unit cost shall also include cost of deshuttering. Double, triple height staging various levels shall not be paid separately and is inclusive of rates.
i | Footings | Sq.m | 200 | 550 | 110000
ii | Columns at all levels | Sq.m | 745 | 650 | 484250
iii | Slabs at all levels | Sq.m | 1125 | 610 | 686250
iv | Beams at all levels | Sq.m | 1562 | 610 | 952820
v | staircase slabs at all levels | Sq.m | 12 | 750 | 9000
vi | cantilever slabs at all levels | Sq.m | 5 | 750 | 3750
vii | Parapet wall at terrace level | Sq.m | 315 | 670 | 211050
xii | Cornices at terarce level | Rmt | 170 | 750 | 127500
| Total for Shuttering works |  | 3964
5 | Reinforcement steel
General Note
Unless otherwise specified rate quoted shall include the following……..
i | Cost of all reinforcement, labour, equipment / tools & plants required, shifting, infrastructure facilities required etc.
ii | Work at any depth below ground level or any height above ground level and at all levels, heights & elevation and location.
iii | All reinforcement steel shall be HYSD steel Fe 500 grade only
iv | Cutting, wastage, straightening, bending, hoisting, fixing, welding, supporting in position, PVC cover blocks, 18 gauge GI binding wire
v | Unless otherwise noted in the bills of Quantities, method of measurements shall be in accordance with IS 1200. Reinforcement shall be measured only in lengths of bars as actually placed in position on standard weight basis, no allowance shall be made in the weight for rolling margin. Authorised laps and splices shall be measured. Chairs of any shape & profiles, Spacer bar of any shape & profile, cover block, wastage and binding wire will not be measured and shall be included in the quoted rates.
vi | Tests on material shall conform to IS Specification and the test shall be carried out as directed either at site Laboratory or at any approved test laboratory.
vii | For measurement & payment, actual quantity for reinforcement bars provided and authentic laps OR couplers provided (but excluding hooks, spacer bars, chairs, pins, laps that are not authentic, temporary fixing & supports etc) shall be measured. The contractor shall take into account the quantities for hooks, spacer bars, chairs, pins, laps that are not authentic, temporary fixing & supports etc complete and quote accordingly. No extra payment on this account shall be considered.
viii | In the event it is observed that the reinforcement is showing sign of rusting / corrosion due to atmospheric effect or during monsoon and the same is not accepted by the Project Manager, then the contractor at his cost shall apply an approved anti corrosive treatment over such steel.
| Supplying, cutting, bending to shape, fabricating, fixing and tying in position Fe500 grade Reinforcement Steel. The reinforcement shall be of approved brands only. No equivalent material shall be entertained. The cost also includes the cost of providing & tying with 18 gauge GI binding wire shall be included in the reinforcement rate. Rate of reinforcement shall also include cost of all related operations, inputs of labour, materials, tools and plants etc complete. | M.T | 73.5 | 83000 | 6100500
All reinforcement shall be preferably in lengths not exceeding 12 meters unless otherwise stated. No allowance has been made in the weights of steel reinforcement for rolling margin or the weight of weld metal.
Total for Reinforcement Works
6 | Membrane & Cementitious waterproofing Works
General Notes
i | Surface Requirement to do the effective waterproofing.
ii | All surfaces to be waterproofed should be made sound, clean and dry.
iii | Concrete surfaces should have a light steel-trowel followed by a fine hair-broom or equivalent finish, which is dry and free of dust, oil and other contamination.
iv | Sharp projection, moss and lichen must be removed physically.
v | Grouting periphery of spout pipes with water insensitive epoxy, pressure grouting of construction joints and honey comb areas with cement grout, proper preparation of the concrete surface by mechanical means / hydro blasting to ensure a good bond between the topping and the substrate.
vi | Testing of the surfaces prior to start the work, grouting or sealing of joints, packing bore holes, making watta (coving) at corners / junctions etc complete.
Important Notes -
i | Specialized agency to be approved by Client / who shall give Guarantee for 10 years for the Waterproofing Works done at Site.
ii | Contractor shall give both material and preformance guarantee in the format approved by Clients / Consultants.
Substructure Waterproofing
6.1 | Lift pit internal waterproofing
i | All surface area should cleaned up to visible of hair cracks / aggregate texture. Cleaning of RCC member should be done by hacking tool, wire brush, wire grinder & air blower etc. Open minor cracks & construction joints should be sealed with cement mortar with additive. All clean & treated area should tested for water tighness by flooding water. All wet spots & water leakage area should mark for treatment. | Sq.m | 21 | 950 | 19950
ii | Providing and applying Vandex BB 75 / Blue Dex or equivalent waterproofing system in two coats by trowelling method. The 1st coat of Blue Dex shall be applied to the prepared surface. Whilst the 1st coat is still “green” a second coat comprising of Blue Dex. The slurry coatings shall be applied with a stiff masonary brush or stiff broom and worked into every irregularity on the surface shall be done by means of trowelling or by spray only. Treatment to floor slabs shall be carried out by trowel application using a steel trowel into hardenced concrete slab surface including curing, cleaning etc complete. (Protection over the membrane not required for this system)
Super Structure W.P
6.2 | Toilet Waterproofing (250mm Sunken)
A | Flooring
i | All surface area should cleaned up to visible of hair cracks / aggregate texture. Cleaning of RCC member should be done by hacking tool, wire brush, wire grinder & air blower etc. Open cracks & construction joints should be sealed with cement mortar with additive Conplast WL / Cebex 100 / repair mortar or equivalent as per manufacturers specification etc complete. All clean & treated area should tested for water tighness by flooding water. All wet spots & water leakage area should mark for treatment. | Sqm | 3.25 | 1250 | 4062.5
ii | Providing and applying primer in one coat at coverage of 6-7 Sqm per Ltr using brush or long nap roller prior to application. Allow the surface to dry completely. Providing and applying single / two component WPM 002 / Blueguard / Revestidan @2.2 kgs / sqm in two coats by Design Engineer, advanced acrylic cementitious modified, fast drying, tough, uniquely formulated with synthetic micro fibers to increase its strength, applying first coat of WPM 002 / Blueguard / Revestidan, sandwiching Deck Web / Chopstrand mat on wet first coat at internal and external corners, allowing it to dry completely, after 4 Hrs time gap, applying second coat of WPM 002 / Blueguard / Revestidan in perpendicular direction to the applied first coat and allowing it to dry completely, etc and complete as per manufacturer's specification. [The membrane shall confirm to:-Elongation at Break : > 150 %; Tensile Strength : > 1 MPa; Water Absorption : 4.3%; Shore A hardness - > 80]
iii | Providing & laying of 25mm thick CM 1:4 protective screed admixed with Conplast WL or equivalent Integral waterproofing compound of approved make as per manufacturers specification.
iv | Sunken Portion:- Providing and laying brick bat waterproofing treatment to deck slab of 200mm sunk. The slab shall be laid over with well burnt brick bats coba laid & joints filled in with cement mortar 1:4 in true lines & levels gradient with minimum 50mm at outlet / nahani trap (for easy flow of water/rain water). Finally the top surface of brick bat coba shall be laid over and joints finished with 20mm waterproofing layer with CM 1:4 and admixture finished rough to receive further finishes. The treated surface after 12 to 15 hrs. shall be kept ponded for continuous period of 10 days to detect any seepage/ leakage/ dampness if any, the surface then shall be cleaned. | cum | 0.8 | 7500 | 6000
B | Walls
i | All surface area should cleaned up to visible of hair cracks / aggregate texture. Cleaning of RCC member should be done by hacking tool, wire brush, wire grinder & air blower etc. Open cracks & construction joints should be sealed with cement mortar with additive Conplast WL / Cebex 100 / repair mortar or equivalent as per manufacturers specification etc complete. All clean & treated area should tested for water tighness by flooding water. All wet spots & water leakage area should mark for treatment. | Sq.m | 7.75 | 1250 | 9687.5
ii | Providing and applying primer in one coat at coverage of 6-7 Sqm per Ltr using brush or long nap roller prior to application. Allow the surface to dry completely. Providing and applying single / two component WPM 002 / Blueguard / Revestidan @2.2 kgs / sqm in two coats by Design Engineer, advanced acrylic cementitious modified, fast drying, tough, uniquely formulated with synthetic micro fibers to increase its strength, applying first coat of WPM 002 / Blueguard / Revestidan, sandwiching Deck Web / Chopstrand mat on wet first coat at internal and external corners, allowing it to dry completely, after 4 Hrs time gap, applying second coat of WPM 002 / Blueguard / Revestidan in perpendicular direction to the applied first coat and allowing it to dry completely, etc and complete as per manufacturer's specification. [The membrane shall confirm to:-Elongation at Break : > 150 %; Tensile Strength : > 1 MPa; Water Absorption : 4.3%; Shore A hardness - > 80]
iii | Providing and applying 10 to 12 mm thick with CM 1:4 for wall plastering admixed with Conplast WL or equivalent integral waterproofing compound etc. complete, as per manufacturer's specifications
iv | Treatment for Core Cutout Area (Upto 150mm dia)
| Grouting & Sealing around the periphery joints of pipes passing through on the floor & walls by filling B30 / Powergrout microconcrete in the gap between the cut cuts in the slab & the pipe surface. | Kg | R.O | 75
v | Collar Treatment providing and fixing drain collar of required size around the pipe sandwitched with waterproofing membrane. | Nos | 2 | 1000 | 2000
vi | Threshold For Toilets Providing and making barrier bund in micro concrete at door sill outside wet areas. (100MM X 25 MM) | Rmt | 0.75 | 5000 | 3750
6.3 | Terrace floor waterproofing
A | Flooring
i | All surface area should cleaned up to visible of hair cracks / aggregate texture. Cleaning of RCC member should be done by hacking tool, wire brush, wire grinder & air blower etc. Open cracks & construction joints should be sealed with cement mortar with additive. All clean & treated area should tested for water tighness by flooding water. All wet spots & water leakage area should mark for treatment. | Sq.m | 695 | 1100 | 764500
ii | Providing and applying Formrok 500 / Bluesil 560 or equivalent A high performance, low odour, one-part, fastcuring,high solids, cold applied polyurethane elastomer waterproof membrane over uniform surface of slab. Apply @ 1.3 kgs/sqm in two coats. Bluesil 560 is a pure polyurethane elastomer. It does not contain bitumen or tar and will not bleed or stain. Bluesil 560 should have following minimum properties: i) Solid % Vol: (89 ± 3) ii) Tensile Strength > 2.0 MPa (ASTM D412) iii) Elongation > 550% (ASTM D412) iv) Shore A Hardness - 30 ± 5 (ASTM D2240) v) Chemical Resistance - Excellent (ASTM C543)
iii | Providing and placing Non woven polyester Geo Textile fabric 100 GSM with minimum 75mm overlap on the ends and sides as a separation layer on the membrane. | Sq.m | 695 | 90 | 62550
iv | Providing and filling avg 125mm thick light weight brick / block bat coba waterproofing treatment to specified areas viz terrace, exposed slabs etc. The slab shall be laid over with brick / block bats coba laid & joints filled in with cement mortar 1:5 in true lines & levels gradient with max thickness of 110mm and required slope at rain over let (for easy flow of water/rain water) Finally the top surface of brick / block bat coba shall be laid over and joints finished with waterproofing layer with CM 1:4 and admixture finished smooth with cement slurry. The treated surface after 12 to 15 hrs. thereafter shall be kept ponded for continuous period of 7 days to detect any seepage/ leakage/ dampness if any, the surface then shall be cleaned to withstand weather and domestic use. (Extra avg thickness over 125mm to be paid extra) | Sq.m | 695 | 1350 | 938250
B | Walls
i | All surface area should cleaned up to visible of hair cracks / aggregate texture. Cleaning of RCC member should be done by hacking tool, wire brush, wire grinder & air blower etc. Open cracks & construction joints should be sealed with cement mortar with additive. All clean & treated area should tested for water tighness by flooding water. All wet spots & water leakage area should mark for treatment. | Sq.m | 87 | 1110 | 96570
ii | Providing and applying Formrok 500 / Bluesil 560 Polyurethane elastomer waterproof membrane, A high performance, low odour, one-part, fastcuring,high solids, cold applied polyurethane elastomer waterproof membrane over uniform surface of slab. Apply @ min 1.5 kgs/sqm in two coats. membrane is pure polyurethane elastomer. Membrane should have following minimum properties: i) Solid % Vol: (65 ± 3) ii) Tensile Strength > 2.0 MPa (ASTM D412) iii) Elongation > 500% (ASTM D412) iv) Shore A Hardness - 30 ± 5 (ASTM D2240) v) Chemical Resistance - Excellent (ASTM C543)
iii | Providing and applying one coat of plaster CM 1:4 of 10-12mm thick and adding conplast WL or equivalent waterproofing compound and curing the same thoroughly. | Sq.m | 87 | 465 | 40455
6.4 | Chajja slab Waterproofing
i | All surface area should cleaned up to visible of hair cracks / aggregate texture. Cleaning of RCC member should be done by hacking tool, wire brush, wire grinder & air blower etc. Open cracks & construction joints should be sealed with cement mortar with additive. All clean & treated area should tested for water tighness by flooding water. All wet spots & water leakage area should mark for treatment. | Sq.m | 13 | 1550 | 20150
ii | Providing and applying Blue HY Seal / Formdex Uni or equivalent brush applied Cementitious elastomeric acrylic water proof coating in in 2 coats to form minimum 0.8mm thick membrane. The Waterproofing System is capable of forming a waterproof barrier around or inside the concrete, complete. Membrane should have following minimum properties: i) Adhesive strength 0.6N/mm2 ii) Elongation >115% (ASTM D412) iii) Pot Life - 60 Minutes iv) Crack Bridging - No Crack at 2mm (ASTM D836) shall be applied as per manufacture specification.
iii | Providing and laying IPS appx. 30mm thick over Chajja in CM 1:3 laid to slope and with proper vatas at junction with false squares, curing testing complete. | Sq.m | 13 | 650 | 8450
Total of Waterproofing work
7 | Miscellaneous Work
7.1 | Breaking & demolition of reinforced cement concrete of any dimension and at any level, manually or by mechanical means as the case may be with necessary tools and plants, scaffolding .The scope includes removal of debris, it's disposing at approved location, loading and unloading and making the surface good etc.complete. The contractor shall cut of steel rods of any dia using gas cutter, stack and hand over the steel to Clients. The entire breaking / dismantling operation shall be carried out as per specific instructions & directions of EIC. (This item shall be operated only in view of any changes in drawings & thereby breaking of structural member is necessary) | Cu.m | R.O | 7500
7.2 | Breaking & demolition of brick work / block work (plastered or unplastered) of any dimension and at any level, manually or by mechanical means as the case may be with necessary tools and plants, scaffolding. The scope includes removal of debris, it's disposing at approved location, loading and unloading and making the surface good etc.complete. The entire breaking / dismantling operation shall be carried out as per specific instructions & directions of EIC. (This item shall be operated only in view of any changes in drawings & there by breaking of structural member is necessary.) | Cu.m | R.O | 3500
Total of Miscellaneous
| TOTAL . . . . |  |  |  | 19877045
| Add for taxes |  |  |  | 3577868.1
| GRAND TOTAL . . . . |  |  |  | 23454913.1
Notes :
a | Contractor to take approval for mix design from Consultant.
b | Above quantities are excluding elevational features like elevational column, band, elevational detail above terrace floor, pediments etc. Its quantities shall be extra over & above these quantities as per the actuals.
c | Quantities indicated herein above is without wastage in case of Concrete & Steel and excluding i) rolling marign ii) chairs, iii) pins iv) spacers v) laps that are not authentic and vi) any additional steel provided as per site condition.

## Internal Civil BOQ
BOQ for CIVIL WORKS OF 11 kVA SUBSTATION, INFRA, NIDP
S.No. | Description | UOM | QTY | Rate | Amount
1 | Masonry Works
Note - Except the lintels over the openings, No bands to be considered in the Hollow Block masonry.
1.1 | Providing & Constructing Hollow Concrete Block Masonry wall in proportion of 50 Kg cement : 175 litres of manufactured sand : 350 ml of approved additives consolidated 9mm to 18mm thick joint with necessary scaffolding, 7 days curing, racking of joints, providing any sleeves for services etc lead & lift to required height. Rate to include providing and fixing reinforcement with two numbers of 8mm Reinforcement steel rods at every third course embedded in mortar, complete as per specifications, Chapkam as per drawings & as directed by the engineer-in charge. Providing vertical stiffener rebar in hollow block masonry to be continued for walls exceeding 36t in length ( t = thickness of wall i.e. 2 nos 12mm dia rebar’s @ 4m c/c or 10mm dia rebar’s @ every 1.5m c/c , to be grouted with mortar having proportion 1 part cement : 2 parts CA 1 : 1 part sand. (only vertical stiffener Reinforcement for this activity will be paid in Reinforcement Item no.2.6) Solid made Hollow Block to be used below window sill & in last layer of block masonry, beside Staircase door side & Electrical duct window side.
Internal Block Work
i | 150 mm thick hollow block work | Sq.m | 1810.77 | 1600 | 2897232
1.2 | Providing and constructing masonry with approved quality solid concrete blocks in proportion of 50 Kg cement : 175 litres of manufactured sand : 300 ml of approved additives consolidated 9mm to 18mm thick joint doing masonry in specified courses, complete with raking out joints, curing, doing independent double legged scaffolding, complete as per specifications etc. at all heights, depths, rate to include as per drawings and leads and as directed by EIC to his entire satisfaction.
Internal Solid Blockwork
ii | 125 mm thick solid block work | Sqm | QRO | 1650
iii | 150 mm thick solid block work | Sqm | QRO | 1750
v | 225 mm thk solid block work | Sqm | QRO | 1850
External Solid Blockwork
ii | 125 mm thick solid block work | Sqm | QRO | 1750
iii | 150 mm thick solid block work | Sqm | QRO | 1850
2 | Plaster
2.1 | Internal Plaster
A | Gypsum Vermiculite Plaster
Providing & applying Gypsum Vermiculite Plaster as per approved make/ brand/ source on Walls 12 mm to 15mm thick and ceiling 8 to 10 mm thick with scaffolding , working tools ,lights to complete in all respect to the satisfaction of EIC including any rectification / repair during start of painting. Work to be carried out with proper level pads and surface preparation. Please refer hand book for detailed method study / workmanship etc.Rate to inlcude providing and applying GP adhesive of approved brand as a bonding agent to RCC surface as specified and location before application of Gypsum vermiculite plaster etc Location:Entrance lobby, lift lobby ground and typical floors
i | Wall-Gypsum Plaster to Blockwork | Sq.m | 894 | 340 | 303960
ii | Wall-Gypsum Plaster with Bonding agent only to RCC surface | Sq.m | QRO
B | Internal Cement Plaster
Providing and applying internal single coat cement plaster avg 12mm to 15mm thk on RCC, masonry walls in required finished with cement mortar at the ratio of 1 cement : 4 fine and coarse sand in equal proportion with finishes like scratch coat finish as directed by the Project Manager to walls, chajjas, loft slabs and / or any other location to its true line and level plumb, right angles etc. complete as per the drawings specification and as directed by the Project Manager. The rate shall also include for making and fixing of level pads, cleaning, and pre-wetting of surface , providing and fixing of bonding agent of Flexicrete from Apurva make or equivalent) at junctions of masonry and concrete members at the junction of RCC and masonry including all consumables, screening of sand and washing, shifting of material to required location , providing , erection, maintaining and dismantling of approved scaffolding at all heights and for all leads, making mortar by using mixer machine,the sand used for mortar shall confirms gradation as per the IS: 1542:1977; Cl.No.3 etc. complete as directed and to the satisfaction to the Project Manager. No extra shall be paid for drip moulds, grooves, corner, bands, cornices etc. The rate shall also include for providing and mixing approved admixtures, finishing of skirting tip ( Judd filling), curing etc. complete as per technical specification and as directed and to the satisfaction of the Project Manager. (mode of measurement payable upto top of skirting for height)
i | Toilet Wall | Sq.m | 26.88 | 390 | 10483.2
2.2 | External Plaster
| Providing and applying minimum 25 mm thick double coat sand faced cement plaster; first coat to be 15 mm thick cement sand mortar of mix ratio CM 1:4 (1 cement : 4 sand) including adding 2% by weight of cement, approved waterproofing compound and polypropylene fibers as per recommandations of approved manufacturer, second coat to be 10 mm thick in cement sand mortar of mix ratio CM 1:3 (1 cement : 3 sand) including adding mechanical mixer 10/7 mixer as per recommandations of approved manufacturer, finished sand face or as required to receive specified architectural external finish to correct line, plumb and level to external faces of walls, sofits/ceiling if any hacking concrete surfaces then applying chemical adhesive coating and a scratch/dash coat as a possitive bond, curing the same, racking out junctions of masonry and concrete, then pointing and grouting using non-shrinking compound, joints grouted by pressing square crushed stone, further providing 150mm wide 24gauge GI chicken mesh at junctions of concrete and masonry work etc. The rate shall also include for making and fixing of level pads, cleaning and pre-wetting of surface, providing and fixing of fiber mesh 150 mm wide as approved by Project Manager at the junction of RCC and masonry including all consumables, screening and washing of sand base coat and for final coat ( pass through 4.75 mm sieve and be retained on 2.36 mm sieve ) shifting of material to the required location, providing erecting, maintaining and dismantling of approved H-frame steel scaffolding (external perimeter and internal ) or movable working platform for all height / levels / leads. Green fiber cloth around the perimeter further along scaffolding to ensure the spreading of mortar to the adjoining areas while working at heights,making machine mix mortar to satisfaction of the Project Manager. No extra shall be paid for drip moulds, grooves, corner, bands, cornices,curing etc. Cost includes providing and applying adhesive coat with approved chemical on RCC surface prior to application of plaster. | Sq.m | 1107 | 690 | 763830
3 | Chamber Construction
I | Construction of chambers as per below specified sizes (LxBxD)(1.8 x 1.8 x 1.5 mtr) in 150 mm thick solid block work complete in all respects as per drawings and details including excavation, backfilling, PCC- M10, Internal Plaster of CM 1:4 (12 to 15 mm thick), top cover in lockable systems as per approved sample and as per directions of EIC complete in all respects (Covers of chambers will be decided & fixed at actuals and are to be fixed as per instructions of EIC) Its rates will be quoted as per actual expenses with 10% profit. | No | 8 | 58000 | 464000
4 | INTERNAL PAINTING
4.1 | Semi Acryilc Emulsion paint
Providing and applying 2 coats of exterior grade Semi Acryilc Emulsion paint of approved make and colour to internal walls.Rate to include surface preparation, filling up and finishing smooth with approved 2 coat of acrylic putty, crack filler / binder; cleaning and making the surface dust-free, applying a sealer or 1 primer coat of approved brand, applying 2 coats of acrylic emulsion paint( backing should not been seen)etc complete to the satisfaction of Project manager. Rate includes scaffolding required for the work,cleaning and removing the debris out of site. .Refer painting scheme drawing and technical specifications
II | Wall | Sqm | 1215.44 | 220 | 267396.8
ii | Ceiling | Sqm | 726 | 190 | 137940
4.2 | White wash
Providing & applying 2 coats of white wash paint to give an even shade( and backing should not been seen) at all lead and lift including scraping, surface cleaning, removing undulations, provision of scaffolding (single/double) including erection and removal etc. complete. (Location: Lift Shaft and ducts).Refer painting scheme drawing and technical specifications
i | Wall & Ceiling | Sqm | 145.53 | 110 | 16008.3
5 | EXTERNAL PAINTING
5.1 | Providing and applying external texure paint - Providing and applying basecoat with Trowel (approved patterned texture) - & two coats of Dirt Resistant and Water Repellant - Acrylic emulsion Paint ( Exterior grade) as per approved colour and as per manufacturers specification.Rate to include scrapping, cleaning the surface with coir/wire brush; the surface must be cleaned with water jets to obtain a dust/loose particle free surface. (Rate is inclusive of providing, erection and dismantling of scaffolding / staging / temporary hoisting).Refer painting scheme drawing, Specifications and Method statement | Sqm | 1194 | 450 | 537300
5.2 | Providing and applying external paint - Providing and applying two coats of Dirt Resistant and Water Repellant Acrylic emulsion Paint ( Exterior grade) as per approved colour and as per manufacturers specification. Rate to include scrapping, cleaning the surface with coir/wire brush; the surface must be cleaned with water jets to obtain a dust/loose particle free surface. (Rate is inclusive of providing, erection and dismantling of scaffolding / staging / temporary hoisting).(location - Precast railing and grills, Cornices and elevation features) .Refer painting scheme drawing, Specifications and Method statement Location: Staircase slab soffit, walls | Sqm | 21.7 | 450 | 9765
5.3 | Providing and applying exterior grade Semi Acrylic Emulsion paint - Providing and applying 2 coats of exterior grade Semi Acrylic Emulsion paint of approved make and colour to internal walls.Rate to include surface preparation, filling up and finishing smooth with approved crack filler / binder; cleaning and making the surface dust-free, applying a sealer or 1 primer coat of approved brand, applying 2 coats of semi acrylic emulsion paint( backing should not been seen)etc complete to the satisfaction of Project manager. Rate includes scaffolding required for the work,cleaning and removing the debris out of site. .Refer painting scheme drawing and technical specifications Location: Terrace side face of Parapet wall | Sqm | 190 | 350 | 66500
6 | Precast RCC Grill
| Providing & fixing RCC precast grills of specified sizes with cement grout as per locations shown in the drawing and as per istructions of EIC. including all consumables, screening of sand and washing, shifting of material to required location , providing , erection, maintaining and dismantling of approved scaffolding at all heights and for all leads, making mortar by using mixer machine,the sand used for mortar shall confirms gradation as per the IS: 1542:1977; Cl.No.3 etc. complete as directed and to the satisfaction to the Project Manager. The rate shall also include for providing and applying approved adhesive like 2 coats of flexicrete, chaat coat, curing etc. complete as per technical specification and as directed and to the satisfaction of the Project Manager. Size - 750 x 750mm | No | 264 | 2000 | 528000
7 | Kota Flooring Work
i | Providing and fixing 2'x2' Kota stone of approved thickness in flooring with semi dry method in 50mm thick 1:6 (cement : river sand) CEMENT MORTAR including 7 coat floor polishing with Suri Polex stones 0 to 5 nos. & final Coat 5X stone of Technique brand with Table top Machine etc. complete as per drg & spec (Basic rate: INR 55 /sft) (Only visible kota stone will be measured, hence rates are to be quoted accordingly) | Sqm | 46.698 | 1050 | 49032.9
ii | Treads (Prepolished & 280 mm width) | Sqm | 8.88 | 1750 | 15540
iii | Riser (Prepolished & 150 - 170 mm height) | Sqm | 5.424 | 1450 | 7864.8
iv | 75 mm Ht Skirting - on both side of flight (Prepolished & approved thk) | RMtr | 17.4 | 175 | 3045
7 | Staircase Railing Fabrication Work
| Providing, supplying, fabricating and fixing MS staircase railing with zin-chromate primer (1 coat) + enamel paint (2 coats) ( Pipe of 3.15 to 3.2mm thickness, guage10-Zenith) in accordance with specification and approved drawings, at all levels & all heights, delivering at site, hoisting and fixing in position, including all temporary staging and supporting work and making all structural steel work. The rate of steel work shall include cutting, grinding, machining, assembly, welding, jointing, building up new sections, cost of fasteners (nuts, bolts and washers) etc complete as per drawing. Rate also include cleaning of MS steel and application of zinc chromate primer (1 coat) + enamel paint (2 coats) as specified and approved make etc complete at all leads, lifts to approval of the Project Manager. | Rmtr | 5.8 | 2500 | 14500
8 | Waterproofing Works
i | Cleaning, surface preparation & ponding test for checking leakage and if any, then repair it with PU sealant as per instructions of EIC. including all consumables, screening of sand and washing, shifting of material to required location , for all leads, making mortar by using mixer machine,the sand used for mortar shall confirms gradation as per the IS: 1542:1977; Cl.No.3 etc. complete as directed and to the satisfaction to the Project Manager. The rate shall also include for providing and applying approved One coat of solvent free epoxy primer PU coat, curing etc. complete as per technical specification and as directed and to the satisfaction of the Project Manager. | Sqm | 264 | 1250 | 330000
ii | Providing and laying screed with M20 concrete induced with microfibers, curing etc. complete as per technical specification and as directed and to the satisfaction of the Project Manager. | Sqm | 774.1834 | 650 | 503219.1938
|  |  |  | S.TOTAL | 6925617.1937
|  |  |  | GST 18 % | 1246611.0949
|  |  |  | G.TOTAL | 8172228.2886

## 220KV AIS SWITCHYARD BOQ
Project | 220KV AIS SWITCHYARD (WITH TWO INCOMERS + EIGHT OUTGOING FEEDERS + DOUBLE BUS - BARS + COUPLER)
Customer
Address | A-119/1, Sector-29, YEIDA, Gautam Budha Nagar, Uttar Pradesh
Contractor | Srex Power India Pvt. Ltd. H-165, Sector-63, Noida-201301, Uttar Pradesh
Document | BILL OF MATERIAL FOR SUPPLY MATERIALS - CIVIL WORK & ERECTION WORK
A | BILL OF MATERIAL FOR SUPPLY MATERIALS
S.NO. | DESCRIPTION | UNIT | QTY | HSN CODE | Unit Rate | Amount | SEQUENCE AS PER PREFERRED MAKE
220KV LINE BAY SUB STATION PLANT SIDE
1 | Supply of 10kA, 198KV Lightning Arrestor with insulating base & surge counter | Nos. | 6 | 85354010 | 65500 | 393000 | CGL / LAMCO/ OBLUM
2 | Supply of 220 kV, 40kA for 3 Sec, PT 220KV/√3/110V/√3/110V/√3 for tariff metering | Nos. | 6 | 85043300 | 320129 | 1920774 | MEHRU / HEPTACARE / CGL / CAPCO
Core -1 - CL: 0.2, 20VA
Core -2 - CL: 0.2, 20VA
3 | Supply of 220 kV, 40kA for 3 Sec., Current Transformer 450/1-1A for tariff metering | Nos. | 6 | 85043300 | 344754 | 2068524 | MEHRU / HEPTACARE / CGL / CAPCO
Core -1 - CL: 0.2S, 20VA
Core -2 - CL: 0.2S, 20VA
4 | Supply of 220 kV, 40kA for 3 Sec., Potential Transformer / CVT 220KV/√3/110V/√3 /110V/√3/110V/√3 for Line Protection | Nos. | 6 | 85043300 | 320129 | 1920774 | MEHRU / HEPTACARE / CGL / CAPCO
Core -1 - CL: 0.2, 50VA
Core -2 - CL: 3P, 50 VA
Core -3 - CL: 3P, 50 VA
5 | Supply of 220kV, 40kA for 3 Sec. Current Transformer 800-400/1-1-1-1-1A for Line Protection | Nos. | 6 | 85043300 | 344754 | 2068524 | MEHRU / HEPTACARE / CGL / CAPCO
Core -1 - CL: PS
Core -2 - CL: PS
Core -3 - CL: 0.2S, 20VA
Core -4 - CL: PS
Core -5 - CL: PS
6 | Supply of 220kV, 1250A, 40kA for 3Sec. outdoor type double break center post, rotating, motorized Isolator with Two earth switch | Sets | 2 | 85353090 | 538678 | 1077356 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
7 | Supply of 220kV, 1250A, 40kA for 3 sec, outdoor type double break centre post rotating, motorized Isolator without Earth switch (Tandem Type) | Sets | 2 | 85353090 | 452489 | 904978 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
8 | Supply of 220kV, 1250A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator without earth switch | Sets | 2 | 85353090 | 434020 | 868040 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
9 | Supply of 220kV, 1250A, 40kA for 3 Sec. pole operated single phase SF6 Circuit Breaker | Sets | 2 | 85352919 | 1600642 | 3201284 | SIEMENS/ CGL/ ABB
10 | Supply of ABT Compliant Energy Meter (MAIN & CHECK) with RS 485 Port for Communication | Sets | 2 | 90283010 | 800885.5 | 1601771 | SECURE/ L&T
11 | Supply of of 220kV Cable Sealing End ( PSS End) | Nos. | 6 | 85366990 | 307816 | 1846896 | RAYCHEM / G & W / 3M
220kV TRANSFORMER BAY
12 | Supply of 10kA, 198KV Lightning Arrestor with insulating base & surge counter | Nos. | 24 | 85354010 | 65500 | 1572000 | CGL / LAMCO/ OBLUM
13 | Supply of 220KV, 40kA for 3 sec, Current Transformer 150/1-1-1-1-1A for Transformer bay protection | Nos. | 24 | 85043300 | 344754 | 8274096 | MEHRU / HEPTACARE / CGL / CAPCO
Core -1 - CL: PS
Core -2 - CL: PS
Core -3 - CL: 0.2S, 20VA
Core -4 - CL: PS
Core -5 - CL: PS
14 | Supply of 220kV, 1250A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator with single earth switch | Sets | 8 | 85353090 | 538678 | 4309424 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
15 | Supply of 220kV, 1250A, 40kA for 3 sec, outdoor type double break centre post rotating, motorized Isolator without Earth switch (Tandem Type) | Sets | 2 | 85353090 | 452489 | 904978 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
16 | Supply of 220kV, 1250A, 40kA for 3Sec. outdoor type double break center post, rotating, motorized Isolator without switch | Sets | 14 | 85353090 | 434020 | 6076280 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
17 | Supply of 220kV, 1600A, 40kA for 3 Sec. pole operated single phase SF6 Circuit Breaker | Sets | 8 | 85352919 | 1600642 | 12805136 | SIEMENS/ CGL/ ABB
18 | Supply of N2 Fire Suppression System for Power Transformer for 220/11KV, 40MVA Power Transformer. | Nos. | 3 | 85049010 | 1292827 | 3878481 | CTR / EASUNN-MR
220KV BUS PT & BUS COUPLER
19 | Supply of 220kV, 40kA for 3 Sec. PT / CVT 220KV/√3/110V/√3/110V/√3 for Bus Potential Transformer | Nos. | 6 | 85043300 | 320129 | 1920774 | MEHRU / HEPTACARE / CGL / CAPCO
Core1 : 0.2, 100 VA
Core2 : 3P, 100VA
20 | Supply of 220kV, 40kA for 3 Sec. Current Transformer 800-400/1-1-1-1-1A for Bus Coupler | Nos. | 3 | 85043300 | 344754 | 1034262 | MEHRU / HEPTACARE / CGL / CAPCO
Core -1 - CL: PS
Core -2 - CL: PS
Core -3 - CL: 0.2, 20VA
Core -4 - CL: PS
Core -5 - CL: PS
21 | Supply of 220kV, 800A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator without earth switch Bus PT | Sets | 2 | 85353090 | 434020 | 868040 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
22 | Supply of 220kV, 1250A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator with single earth switch for Bus Coupler | Sets | 2 | 85353090 | 538678 | 1077356 | GR POWER / S&S / ELECTROLITE / GK ELECTRICAL
23 | Supply of 220kV, 1250A, 40kA for 3 Sec. pole operated single phase SF6 Circuit Breaker for Bus Coupler | Set | 1 | 85352919 | 1600642 | 1600642 | SIEMENS/ CGL/ ABB
24 | Supply of 220kV, 6 KN Bus Post Insulator (BPI) | Lot | 1 | 85462040 | 2240000 | 2240000 | IEC / ADITYA BIRLA / HV INSUALTOR
RELAY & CONTROL PANELs
25 | Supply of 220kV Control & Relay Panel for Line Protection | Sets | 2 | 85372000 | 2251400 | 4502800 | SIEMENS/ NELUMBO /DANISH/ABB
0
26 | Supply of 220kV Control & Relay Panel for Transfomer Protection | Sets | 8 | 85372000 | 2008000 | 16064000 | SIEMENS/ NELUMBO /DANISH/ABB
27 | 220kV Control & Relay Panel for Bus Coupler Protection | Set | 1 | 85372000 | 1764600 | 1764600 | SIEMENS/ NELUMBO /DANISH/ABB
28 | Supply of 220kV Control & Relay Panel for Centralized BUSBAR Protection Panel | Set | 1 | 85372000 | 2008000 | 2008000 | SIEMENS/ NELUMBO /DANISH/ABB
29 | Supply of SCADA for Control & Monitoring of Switchyard | Set | 1 | 85372000 | 5841300 | 5841300 | SIEMENS/ NELUMBO /DANISH/ABB
220kV SWITCHYARD HARDWARE MATERIAL
30 | Supply of ACSR Conductor | Lot | 1 | 76141000 | 4268500 | 4268500 | DYNAMIC / KJV ALLOY / APAR
31 | Supply of String Insulators | Lot | 1 | 85462040 | 4162500 | 4162500 | IEC / ADITYA BIRLA / HV INSUALTOR
32 | Supply of Galvanised Steel Structure for equipments Support, gantries tower & Beam etc | Lot | 1 | 73082000 | 34662400 | 34662400 | SALASAR / HS / VINAYAK / VIJAY
33 | Supply of Clamps & Connectors for Switchyard equipment | Lot | 1 | 85049010 | 1356300 | 1356300 | LEGION / ZORDAR / AUMNI TRANSMISSION / PRECICAST
34 | Supply of LT Power & Control cables with suitable Terminations for switchyard equipments | Lot | 1 | 85446090 | 12880400 | 12880400 | KEI/ POLYCAB/ KEC/BONTON
35 | Supply of Earthing of complete switchyard
35.1 | MS Rod | Lot | 1 | 72149979 | 12512600 | 12512600 | SALASAR / HS / VINAYAK / VIJAY
35.2 | GI Strip | Lot | 1 | 73082000 | 9600000 | 9600000 | SALASAR / HS / VINAYAK / VIJAY
36 | Supply of 415V ACDB for yard auxiliary load | Sets | 11 | 85371000 | 112000 | 1232000 | NITYA / INOVATE / RST
37 | Supply of of 5KVA UPS With 220V DC Power Pack with 1 Hour Beak up | Sets | 11 | 85044090 | 146500 | 1611500 | CONSUL NEOWATT / 3EM POWER / EATON / EMERSON
38 | Supply of Internal illumination for Only Control & relay Room Building (LED LIGHT FIXTURES, Ceeling fan & exhaust fan) with 10Nos. 2Tonn. 3star Air Conditioners. Only Control Room Building Tentative size (10m X 15M)
38.1 | Supply of LED Lighting Fixtures etc. | Lot | 1 | 94051090 | 489460 | 489460 | WIPRO / BAJAJ / PHILIPPS / CROMPTON / HALONIX
38.2 | Supply of 10Nos. 2Tonn. 3star Air Conditioners | Lot | 1 | 84151090 | 480000 | 480000 |  | 84151090
39 | Supply of Complete illumination & Lighting of Yard with LCLM with LED LIGHT FIXTURES)
39.1 | LCLM tower / Mast | Lot | 1 | 73082000 | 3950750 | 3950750 | SALASAR / HS / VINAYAK / VIJAY
39.2 | LED LIGHT FIXTURES for LCLM | Lot | 1 | 94051090 | 551900 | 551900 | WIPRO / BAJAJ / PHILIPPS / CROMPTON / HALONIX
40 | Supply of of Lightning protection System for switchyard & Only Control Room Building Tentative size (10m X 15M) | Lot | 1 | 73082000 | 224700 | 224700 | REPUTED
41 | Supply of Complete Fire & Safety Equipments for switchyard (Portable Type) | Lot | 1 | 85354010 | 174400 | 174400 | REPUTED
42 | Supply of Fire Alarm System addressable type conventional smoke detector for Only Control Room Building Tentative size (10m X 15M) | Lot | 1 | 85371000 | 844300 | 844300 | Ravel Fire / Notifier / DS Fire Systems
43 | Supply of FRP Cable tray along with SS Heardwear supports | Lot | 1 | 73012090 | 1860900 | 1860900 | SUMIP COMPOSITES PVT.LTD/PP COMPOSITES PVT. LTD/ FIBERTECH/MAXIMA FRP/ SAYTAM COMPOSITE PVT. LTD
44 | Supply of 220KV Bay Marshalling Kiosk | Nos. | 11 | 85371000 | 110300 | 1213300 | NITYA / INOVATE / RST
45 | Supply of Junction Box
i | Junction Box for 220kV CT's suitable for outdoor installation. | Nos. | 11 | 85371000 | 54000 | 594000 | NITYA / INOVATE / RST
ii | Junction Box for 220kV CVT / PT's suitable for outdoor installation. | Nos. | 4 | 85371000 | 54000 | 216000 | NITYA / INOVATE / RST
| TOTAL-SUPPLY MATERIAL FOR 220/11kV SWITCHYARD |  |  |  |  | 187500000
| OPTIONAL PRICE FOR FOTE TOTAL |  |  |  |  | 7380000
B | BILL OF MATERIAL FOR CIVIL WORK
S.NO. | DESCRIPTION | UNIT | QTY | SAC CODE | UNIT RATE | AMOUNT | Remarks
47 | Civil works for 220/11KV Switchyard
a | RCC Foundation with Rail for 220KV/11KV, 40MVA Power Transformers | Nos. | 8 | 995426 | 650000 | 5200000
b | Construction of RCC Foundation for Nitrogen Purging system panel for 220KV/11KV, 40MVA Power Transformers | Nos. | 8 | 995426 | 50000 | 400000
c | Construction Oil Soak Pit | Nos. | 8 | 995426 | 25000 | 200000
d | Construction of Common RCC Burnt oil tank | Nos. | 1 | 995426 | 1250000 | 1250000
e | Transformer fire wall between 220/11KV, 40MVA Power ransformers | Nos. | 7 | 995426 | 640000 | 4480000
Construction of RCC foundation for following 220KV Outdoor equipments
f | RCC Foundation for 220kV Circuit Breaker | Nos. | 11 | 995426 | 125000 | 1375000
g | RCC Foundation for 220kV Isolators | Sets | 34 | 995426 | 125000 | 4250000
h | RCC Foundation for 220kV Lightning Arrestors | Nos. | 30 | 995426 | 98000 | 2940000
i | RCC Foundation for 220kV Potential transformer /CVT | Nos. | 18 | 995426 | 98000 | 1764000
j | RCC Foundation for 220kV Current Transformer | Nos. | 39 | 995426 | 98000 | 3822000
k | RCC Foundation for 220kV BPI | Lot | 1 | 995426 | 2550000 | 2550000
l | RCC Foundation for 220kV Cable Sealing End (from GSS end to PSS End) | Nos. | 6 | 995426 | 98000 | 588000
m | RCC Foundation for 220kV tower | Nos. | 29 | 995426 | 200000 | 5800000
n | Foundation of LCLM mast | Lot | 1 | 995426 | 420000 | 420000
o | Jelly metal spreading 40 / 20mm jelly | Lot | 1 | 995426 | 550000 | 550000
p | Anti Weed Treatment | Job | 1 | 995426 | 56500 | 56500
q | Construction of Cable Trench Tray Araangement | Lot | 1 | 995426 | 1965000 | 1965000
r | 4M Wide RCC Road inside switchyard | RM | 125 | 995426 | 8500 | 1062500
s | Rain Water Harvesting Arrangement | Lot | 1 | 995426 | 400000 | 400000
t | Drainage Arrangement | Lot | 1 | 995426 | 927000 | 927000
0
| TOTAL-CIVIL CONSTRUCTION OF 220/11kV SWITCHYARD FOUNDATION |  |  |  |  | 40000000
C | BILL OF MATERIAL FOR ERECTION WORK
S.NO. | DESCRIPTION | UNIT | QTY | SAC CODE | Unit Rate | Amount
220KV LINE BAY SUB STATION PLANT SIDE
1 | Installation of 10kA, 198KV Lightning Arrestor with insulating base & surge counter | Nos. | 6 | 995461 | 8421 | 50526
2 | Installation of 220 kV, 40kA for 3 Sec, PT 220KV/√3/110V/√3/110V/√3 for tariff metering | Nos. | 6 | 995461 | 12631 | 75786
Core -1 - CL: 0.2, 20VA
Core -2 - CL: 0.2, 20VA
3 | Installation of 220 kV, 40kA for 3 Sec., Current Transformer 450/1-1A for tariff metering | Nos. | 6 | 995461 | 12631 | 75786
Core -1 - CL: 0.2S, 20VA
Core -2 - CL: 0.2S, 20VA
4 | Installation of 220 kV, 40kA for 3 Sec., Potential Transformer / CVT 220KV/√3/110V/√3 /110V/√3/110V/√3 for Line Protection | Nos. | 6 | 995461 | 12631 | 75786
Core -1 - CL: 0.2, 50VA
Core -2 - CL: 3P, 50 VA
Core -3 - CL: 3P, 50 VA
5 | Installation of 220kV, 40kA for 3 Sec. Current Transformer 800-400/1-1-1-1-1A for Line Protection | Nos. | 6 | 995461 | 12631 | 75786
Core -1 - CL: PS
Core -2 - CL: PS
Core -3 - CL: 0.2S, 20VA
Core -4 - CL: PS
Core -5 - CL: PS
6 | Installation of 220kV, 1250A, 40kA for 3Sec. outdoor type double break center post, rotating, motorized Isolator with Two earth switch | Sets | 2 | 995461 | 12631 | 25262
7 | Installation of 220kV, 1250A, 40kA for 3 sec, outdoor type double break centre post rotating, motorized Isolator without Earth switch (Tandem Type) | Sets | 2 | 995461 | 12631 | 25262
8 | Installation of 220kV, 1250A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator without earth switch | Sets | 2 | 995461 | 12631 | 25262
9 | Installation of 220kV, 1250A, 40kA for 3 Sec. pole operated single phase SF6 Circuit Breaker | Sets | 2 | 995461 | 12631 | 25262
10 | Installation of ABT Compliant Energy Meter (MAIN & CHECK) with RS 485 Port for Communication | Sets | 2 | 995461 | 13048 | 26096
11 | Installation of 220kV Cable Sealing End ( PSS End) | Nos. | 6 | 995461 | 12631 | 75786
220kV TRANSFORMER BAY
12 | Installation of 10kA, 198KV Lightning Arrestor with insulating base & surge counter | Nos. | 24 | 995461 | 8421 | 202104
13 | Installation of 220KV, 40kA for 3 sec, Current Transformer 150/1-1-1-1-1A for Transformer bay protection | Nos. | 24 | 995461 | 12631 | 303144
Core -1 - CL: PS
Core -2 - CL: PS
Core -3 - CL: 0.2S, 20VA
Core -4 - CL: PS
Core -5 - CL: PS
14 | Installation of 220kV, 1250A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator with single earth switch | Sets | 8 | 995461 | 12631 | 101048
15 | Installation of 220kV, 1250A, 40kA for 3 sec, outdoor type double break centre post rotating, motorized Isolator without Earth switch (Tandem Type) | Sets | 2 | 995461 | 12631 | 25262
16 | Installation of 220kV, 1250A, 40kA for 3Sec. outdoor type double break center post, rotating, motorized Isolator without switch | Sets | 14 | 995461 | 12631 | 176834
17 | Installation of 20kV, 1600A, 40kA for 1Sec. pole operated single phase SF6 Circuit Breaker | Sets | 8 | 995461 | 12631 | 101048
18 | Installation of 220/11kV, 40MVA, ONAN, OLTC: -10% to +10%, 1.25%, Z%: 12.5%, Ynyn0 Power Transformer | Nos. | 3 | 995461 | 947369 | 2842107
19 | Installation of N2 Fire Suppression System for Power Transformer for 220/11KV, 40MVA Power Transformer. | Nos. | 3 | 995461 | 68421 | 205263
220KV BUS PT & BUS COUPLER
20 | Installation of 220kV, 40kA for 3 Sec. PT / CVT 220KV/√3/110V/√3/110V/√3 for Bus Potential Transformer | Nos. | 6 | 995461 | 12631 | 75786
Core1 : 0.2, 100 VA
Core2 : 3P, 100VA
21 | Installation of 220kV, 40kA for 3 Sec. Current Transformer 800-400/1-1-1-1-1A for Bus Coupler | Nos. | 3 | 995461 | 12631 | 37893
Core -1 - CL: PS
Core -2 - CL: PS
Core -3 - CL: 0.2, 20VA
Core -4 - CL: PS
Core -5 - CL: PS
22 | Installation of 220kV, 800A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator without earth switch Bus PT | Sets | 2 | 995461 | 12631 | 25262
23 | Installation of 220kV, 1250A, 40kA for 3 Sec. outdoor type double break center post, rotating, motorized Isolator with single earth switch for Bus Coupler | Sets | 2 | 995461 | 12631 | 25262
24 | Installation of 220kV, 1250A, 40kA for 3 Sec. pole operated single phase SF6 Circuit Breaker for Bus Coupler | Set | 1 | 995461 | 12631 | 12631
25 | Installation of 220kV, 6 KN Bus Post Insulator (BPI) | Lot | 1 | 995461 | 54756 | 54756
RELAY & CONTROL PANELs
26 | Installation of 220kV Control & Relay Panel for Line Protection | Sets | 2 | 995461 | 10500 | 21000
27 | Installation of 220kV Control & Relay Panel for Transfomer Protection | Sets | 8 | 995461 | 10500 | 84000
28 | Installation of 220kV Control & Relay Panel for Bus Coupler Protection | Set | 1 | 995461 | 10500 | 10500
29 | Installation of 220kV Control & Relay Panel for Centralized BUSBAR Protection Panel | Set | 1 | 995461 | 10500 | 10500
30 | Installation of SCADA for Control & Monitoring of Switchyard | Set | 1 | 995461 | 50500 | 50500
220kV SWITCHYARD HARDWARE MATERIAL
31 | Installation of ACSR Conductor | Lot | 1 | 995461 | 315800 | 315800
32 | Installation of string Insulators | Lot | 1 | 995461 | 26300 | 26300
33 | Installation of Galvanised Steel Structure for equipments Support, gantries tower & Beam etc | Lot | 1 | 995461 | 2706800 | 2706800
34 | Installation of Clamps & Connectors for Switchyard equipment | Lot | 1 | 995461 | 21100 | 21100
35 | Laying of LT Power & Control cables with suitable Terminations for switchyard equipments | Lot | 1 | 995461 | 121100 | 121100
36 | Installation of Earthing of complete switchyard | Lot | 1 | 995461 | 1276200 | 1276200
37 | Installation of 415V ACDB for yard auxiliary load | Sets | 11 | 995461 | 1600 | 17600
38 | Installation of 5KVA UPS With 220V DC Power Pack with 1Hour Beak up | Sets | 11 | 995461 | 1600 | 17600
39 | Installation of Internal illumination for Only Control & relay Room Building (LED LIGHT FIXTURES, Ceeling fan & exhaust fan) with 10Nos. 2Tonn. 3star Air Conditioners. Only Control Room Building Tentative size (10m X 15M)
39.1 | Installation of LED Lighting Fixtures etc. | Lot | 1 | 995461 | 30000 | 30000
39.2 | Installation of 10Nos. 2Tonn. 3star Air Conditioners | Lot | 1 | 995461 | 38400 | 38400
40 | Installation of Complete illumination & Lighting of Yard with LCLM with LED LIGHT FIXTURES)
40.1 | Installation of LCLM tower / Mast | Lot | 1 | 995461 | 177600 | 177600
40.2 | Installation of LED LIGHT FIXTURES for LCLM | Lot | 1 | 995461 | 25000 | 25000
41 | Installation of Lightning protection System for switchyard & Only Control Room Building Tentative size (10m X 15M) | Lot | 1 | 995461 | 15800 | 15800
42 | Installation of Complete Fire & Safety Equipments for switchyard (Portable Type) | Lot | 1 | 995461 | 10500 | 10500
43 | Installation of Fire Alarm System addressable type conventional smoke detector for Only Control Room Building Tentative size (10m X 15M) | Lot | 1 | 995461 | 31600 | 31600
44 | Installation of FRP Cable tray along with SS Heardwear supports | Lot | 1 | 995461 | 140800 | 140800
45 | Installation of 220KV Bay Marshalling Kiosk | Nos. | 11 | 995461 | 5300 | 58300
46 | Installation of Junction Box
i | Junction Box for 220kV CT's suitable for outdoor installation. | Nos. | 11 | 995461 | 3200 | 35200
ii | Junction Box for 220kV CVT / PT's suitable for outdoor installation. | Nos. | 4 | 995461 | 3200 | 12800
| TOTAL 220/11kV SWITCHYARD MATERIAL ERECTION |  |  |  |  | 10000000
| GRAND TOTAL AMOUNT SUPPLY+CIVIL + ERECTION (A+B+C) |  |  |  |  | 237500000
A1 | BILL OF MATERIAL FOR OPTIONAL PRICE FOR FOTE
1 | Supply of FOTE system only PSS side. | Set | 1 | 85176260 | 7380000 | 7380000 | SIEMENS /ABB / LYCAST
2 | Supply of 250AH, 48V DC Battery and Battery Charger with DCDB for FOTE only PSS side. | Set | 1 | 85072000 |  |  | BATTERY - AMARARAJA / EXIDE CHARGER - AMARARAJA / STATCON / HBL / VOLTSTAT
| TOTAL |  |  |  |  | 7380000
C1 | ERECTION FOR OPTIONAL PRICE FOR FOTE
1 | Installation of FOTE system only PSS side. | Set | 1 | 995461 | 90000 | 90000
2 | Installation of 250AH, 48V DC Battery and Battery Charger with DCDB for FOTE only PSS side. | Set | 1 | 995461 | 30000 | 30000
| TOTAL |  |  |  |  | 120000
| GRAND TOTAL AMOUNT SUPPLY+ ERECTION OF OPTIONAL ITEM |  |  |  |  | 7500000
Note:
1. Bill of Material
The Bill of Material with item Prices are the approximate prices based on the initial estimate. The detail Billing breakup shall be submitted with prices post engineering, however the total quoted price of the offer shall remain unchanged.
2. Make List
We are submitting makes in the last column of the price breakup, Makes are in the preference sequence, more or less we will adhere with most preferred make.However in case of any variation from the preferred make, SPIPL will take prior approval from YOTTA for the same.